## BuildingSummary
Building Summary Medium Office new construction
|  | Value | Data Source
Program
| Building Name | Medium Office Reference Building new construction 90.1-2004
| Available Fuel Types | gas, electricity
| Principal Building Activity | Office
Form
| Total Floor Area (m2) | 4982.2 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 3
Window Fraction (Window to Wall Ratio)
| South | 0.33
| East | 0.33
| North | 0.33
| West | 0.33
| Total | 0.33
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones on each floor
| Floor to Ceiling Height (m) | 2.74
| Floor to Floor Height (m) | 3.96
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel frame | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1977.67
| Net Dimensions - Total Area (m2) | 1324.84
| Wall to Skin Ratio | 0.544
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1661
| Net Dimensions - Total Area (m2) | 1661
| Roof to Skin Ratio | 0.456
Window Dimensions (m2)
| South | 195.85
| East | 130.57
| North | 195.85
| West | 130.57
| Total Area (m2) | 652.84
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 1661
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 1423.65
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 9964.31
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.2 | See Reference Buildings Technical Report
HVAC
| System Type | MZ-VAV | 2003 CBECS
| Heating Type | Gas furnace and electric reheat | 2003 CBECS
| Cooling Type | PACU | 2003 CBECS
| Fan Control | Variable | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 80 | Standard 90.1-2004
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 174.59

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Perimeter_bot_ZN_3 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 10.7639 | 10.7639 |  |  | 10 |  | 111.5894 |  | 0.262
Perimeter_bot_ZN_2 | Yes | 1 | 131.26 | 360.08 | 2.7433 | 91.2801 | 43.52 | 18.5806 | 7.0643 | 10.7639 | 10.7639 |  |  | 10 |  | 70.6435 |  | 0.2759
Perimeter_bot_ZN_1 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 10.7639 | 10.7639 |  |  | 10 |  | 111.5894 |  | 0.262
Perimeter_bot_ZN_4 | Yes | 1 | 131.25 | 360.05 | 2.7432 | 91.2801 | 43.52 | 18.5806 | 7.0638 | 10.7639 | 10.7639 |  |  | 10 |  | 70.6381 |  | 0.27592
Core_bottom | Yes | 1 | 983.54 | 2698.04 | 2.7432 | 0 | 0 | 18.5806 | 52.9336 | 10.7639 | 10.7639 |  | 37.4755 | 10 |  | 529.3363 |  | 0
Perimeter_mid_ZN_3 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 10.7639 | 10.7639 |  |  | 10 |  | 111.5894 |  | 0.262
Perimeter_mid_ZN_2 | Yes | 1 | 131.26 | 360.08 | 2.7433 | 91.2801 | 43.52 | 18.5806 | 7.0643 | 10.7639 | 10.7639 |  |  | 10 |  | 70.6435 |  | 0.2759
Perimeter_mid_ZN_1 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 10.7639 | 10.7639 |  |  | 10 |  | 111.5894 |  | 0.262
Perimeter_mid_ZN_4 | Yes | 1 | 131.25 | 360.05 | 2.7432 | 91.2801 | 43.52 | 18.5806 | 7.0638 | 10.7639 | 10.7639 |  |  | 10 |  | 70.6381 |  | 0.27592
Core_mid | Yes | 1 | 983.54 | 2698.04 | 2.7432 | 0 | 0 | 18.5806 | 52.9336 | 10.7639 | 10.7639 |  | 37.4755 | 10 |  | 529.3363 |  | 0
Perimeter_top_ZN_3 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 10.7639 | 10.7639 |  |  | 10 |  | 111.5894 |  | 0.262
Perimeter_top_ZN_2 | Yes | 1 | 131.26 | 360.08 | 2.7433 | 91.2801 | 43.52 | 18.5806 | 7.0643 | 10.7639 | 10.7639 |  |  | 10 |  | 70.6435 |  | 0.2759
Perimeter_top_ZN_1 | Yes | 1 | 207.34 | 568.77 | 2.7432 | 136.9201 | 65.2801 | 18.5806 | 11.1589 | 10.7639 | 10.7639 |  |  | 10 |  | 111.5894 |  | 0.262
Perimeter_top_ZN_4 | Yes | 1 | 131.25 | 360.05 | 2.7432 | 91.2801 | 43.52 | 18.5806 | 7.0638 | 10.7639 | 10.7639 |  |  | 10 |  | 70.6381 |  | 0.27592
Core_top | Yes | 1 | 983.54 | 2698.04 | 2.7432 | 0 | 0 | 18.5806 | 52.9336 | 10.7639 | 10.7639 |  | 37.4755 | 10 |  | 529.3363 |  | 0
Firstfloor_plenum | No | 1 | 1660.73 | 2024.76 | 1.2192 | 202.8402 | [11 empty] | 0.10903
Midfloor_plenum | No | 1 | 1660.73 | 2024.76 | 1.2192 | 202.8402 | [11 empty] | 0.10903
Topfloor_plenum | No | 1 | 1660.73 | 2024.76 | 1.2192 | 202.8402 | [11 empty] | 1.0017
Total Conditioned Zones |  |  | 4982.19 | 19741.41 |  | 1977.7218 | 652.8006 |  | 268.139
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Commercial Reference Buildings Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 31.9373 | 200.4848 | 72.0444 | 188.9275 |  | 176.4374 | 33.513 | 293.5454 | 8.9823 | 48.3147 | 261.4197 | 84.3871 | 73.6319 | 8.5933 | 8.1354 | 1.6864
Fabric | [6 empty] | weighting factor is for all of 3B
Exterior walls
| Construction Type | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame
| R-value (m2·K / W) | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 1.4205 | 2.0964 | 2.0964 | 2.0964 | 2.0964 | 2.7548 | 2.7548
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
| SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.212
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| VAV_1_COOLC DXCOIL | 140.3 | 139.5318 | 131.6647 | 126.2289 | 102.9237 | 108.1546 | 107.412 | 131.714 | 114.9604 | 103.5668 | 128.8097 | 110.9933 | 126.7537 | 108.2407 | 114.8837 | 84.3167
| VAV_2_COOLC DXCOIL | 138.8079 | 135.9437 | 140.9226 | 127.5096 | 104.3147 | 118.2189 | 120.1299 | 133.0883 | 125.5236 | 116.901 | 130.8089 | 121.7916 | 130.1197 | 120.7652 | 123.5278 | 105.3349
| VAV_3_COOLC DXCOIL | 144.1091 | 151.1019 | 156.4129 | 137.6802 | 108.43 | 132.0381 | 119.449 | 145.3431 | 131.4876 | 118.6863 | 133.6051 | 123.9248 | 131.8862 | 121.5681 | 129.3744 | 104.0484
Heating (kW)
| VAV_1_HEATC | 20.1188 | 21.2251 | 13.5887 | 27.5658 | 10.385 | 19.8201 | 13.9308 | 33.0335 | 24.4456 | 24.3586 | 45.3422 | 35.3635 | 51.9587 | 47.7724 | 54.5616 | 76.6432
| VAV_2_HEATC | 7.1441 | 20.9399 | 12.2638 | 27.0893 | 10.0644 | 18.3922 | 12.7326 | 32.3571 | 23.6271 | 23.12 | 44.5558 | 34.5285 | 51.1392 | 46.7498 | 53.1556 | 74.6964
| VAV_3_HEATC | 6.5964 | 20.2079 | 11.2722 | 26.4233 | 9.9396 | 17.6667 | 12.7971 | 31.748 | 23.1648 | 22.9548 | 44.2573 | 34.3629 | 50.9358 | 46.6832 | 53.0568 | 74.8144
HVAC Efficiency
Air Conditioning (COP)
| VAV_1_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
| VAV_2_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
| VAV_3_COOLC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
Heating Efficiency (%)
| VAV_1_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78
| VAV_2_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78
| VAV_3_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78
HVAC Control - Economizer
| VAV_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| VAV_1_FAN | 6.55 | 6.62 | 6.61 | 6.18 | 5.79 | 5.92 | 6.49 | 6.44 | 6.94 | 6.26 | 6.33 | 6.71 | 6.4 | 6.54 | 6.51 | 5.09
| VAV_2_FAN | 6.68 | 6.8 | 7.5 | 6.5 | 6 | 6.91 | 7.26 | 6.88 | 7.58 | 7.06 | 6.84 | 7.36 | 6.94 | 7.3 | 7.46 | 6.36
| VAV_3_FAN | 7.03 | 7.27 | 8.16 | 6.94 | 6.08 | 7.41 | 7.22 | 7.27 | 7.94 | 7.17 | 7.04 | 7.49 | 7.08 | 7.34 | 7.53 | 6.29
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.085755 | 0.11495 | 0.097061 | 0.098561 | 0.12834 | 0.10058 | 0.14648 | 0.079307 | 0.037203 | 0.078666 | 0.087368 | 0.037205 | 0.062791 | 0.080368 | 0.063024 | 0.10268
| Total Cost ($/m2) | 13.63 | 18.07 | 15.52 | 14.32 | 16.36 | 14.84 | 19.62 | 12.04 | 5.23 | 10.92 | 13.14 | 5.19 | 9.87 | 11.81 | 9.99 | 17.95
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011455 | 0.0081453 | 0.0085525 | 0.00999 | 0.0083959 | 0.0080204 | 0.0084288 | 0.0097698 | 0.0070105 | 0.008372 | 0.008317 | 0.0069141 | 0.007956 | 0.0080072 | 0.0079167 | 0.0041075
| Total Cost ($/m2) | 0.05 | 0.07 | 0.04 | 0.16 | 0.05 | 0.05 | 0.06 | 0.25 | 0.09 | 0.11 | 0.4 | 0.2 | 0.66 | 0.42 | 0.76 | 0.91
Total Utility Costs
| Cost Intensity ($/m2) | 13.68 | 18.14 | 15.57 | 14.48 | 16.41 | 14.89 | 19.68 | 12.29 | 5.32 | 11.03 | 13.54 | 5.39 | 10.53 | 12.24 | 10.75 | 18.87
Energy - End Uses
Electricity (kWh)
| Heating | 4102.7778 | 46805.5556 | 39858.3333 | 58108.3333 | 14808.3333 | 36491.6667 | 81716.6667 | 106202.7778 | 64841.6667 | 114755.5556 | 132113.8889 | 89030.5556 | 173330.5556 | 146777.7778 | 209038.8889 | 311047.2222
| Cooling | 234680.5556 | 186177.7778 | 201908.3333 | 118130.5556 | 75355.5556 | 146477.7778 | 38866.6667 | 101836.1111 | 83616.6667 | 31033.3333 | 69602.7778 | 56708.3333 | 61277.7778 | 37163.8889 | 31513.8889 | 13897.2222
| Interior Lighting | 168400 | 168400 | 168400 | 168400 | 168400 | 168400 | 168400 | 168400 | 168400 | 168400 | 168400 | 168400 | 168400 | 168400 | 168400 | 168400
| Exterior Lighting | 64708.3333 | 64683.3333 | 64672.2222 | 64661.1111 | 64611.1111 | 64597.2222 | 64630.5556 | 64591.6667 | 64616.6667 | 64488.8889 | 64602.7778 | 64563.8889 | 64561.1111 | 64544.4444 | 64508.3333 | 64113.8889
| Interior Equipment | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556 | 296255.5556
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 23405.5556 | 21016.6667 | 25675 | 18433.3333 | 15747.2222 | 22758.3333 | 17363.8889 | 18811.1111 | 22744.4444 | 16552.7778 | 18186.1111 | 20091.6667 | 19077.7778 | 19141.6667 | 19838.8889 | 17338.8889
| Pumps | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 791630.5556 | 783413.8889 | 796841.6667 | 724063.8889 | 635252.7778 | 735055.5556 | 667308.3333 | 756172.2222 | 700550 | 691561.1111 | 749236.1111 | 695125 | 782977.7778 | 732358.3333 | 789630.5556 | 871127.7778
Gas (MJ)
| Heating | 50 | 14210 | 1520 | 47760 | 60 | 6660 | 1290 | 95780 | 33810 | 28770 | 202810 | 106160 | 375920 | 224880 | 435720 | 1061830
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 22720 | 26650 | 24380 | 30450 | 29720 | 27110 | 32970 | 33440 | 32870 | 34990 | 36060 | 35920 | 38330 | 38740 | 42060 | 46580
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 22770 | 40870 | 25900 | 78210 | 29780 | 33770 | 34260 | 129220 | 66680 | 63770 | 238870 | 142080 | 414240 | 263610 | 477780 | 1108410
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 2872640 | 2861150 | 2894530 | 2684840 | 2316700 | 2679970 | 2436570 | 2851440 | 2588660 | 2553390 | 2936120 | 2644530 | 3232960 | 2900110 | 3320450 | 4244470
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 2.9646 | 33.8205 | 28.8006 | 41.9876 | 10.7001 | 26.3679 | 59.0463 | 76.7393 | 46.8529 | 82.9194 | 95.462 | 64.3311 | 125.2441 | 106.0578 | 151.046 | 224.7546
| Cooling (elec) | 169.574 | 134.5272 | 145.8937 | 85.358 | 54.45 | 105.841 | 28.084 | 73.5841 | 60.4192 | 22.4239 | 50.2931 | 40.976 | 44.2777 | 26.8537 | 22.7711 | 10.0418
| Interior Lighting (elec) | 121.6814 | 121.6814 | 121.6814 | 121.6814 | 121.6814 | 121.6814 | 121.6814 | 121.6814 | 121.6814 | 121.6814 | 121.6814 | 121.6814 | 121.6814 | 121.6814 | 121.6814 | 121.6814
| Exterior Lighting (elec) | 46.7565 | 46.7385 | 46.7305 | 46.7224 | 46.6863 | 46.6763 | 46.7003 | 46.6722 | 46.6903 | 46.598 | 46.6803 | 46.6522 | 46.6502 | 46.6381 | 46.612 | 46.327
| Interior Equipment (elec) | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665 | 214.0665
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 16.9122 | 15.1861 | 18.5521 | 13.3194 | 11.3785 | 16.4446 | 12.5467 | 13.5924 | 16.4345 | 11.9606 | 13.1408 | 14.5177 | 13.7851 | 13.8313 | 14.3351 | 12.5286
| Pumps (elec) | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193 | 0.054193
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 572.0115 | 566.0744 | 575.7769 | 523.1896 | 459.017 | 531.1319 | 482.1795 | 546.3902 | 506.1991 | 499.7039 | 541.3784 | 502.2791 | 565.7592 | 529.1829 | 570.5664 | 629.4541
Gas (MJ/m2)
| Heating (gas) | 0.010036 | 2.8522 | 0.30509 | 9.5861 | 0.012043 | 1.3368 | 0.25892 | 19.2245 | 6.7862 | 5.7746 | 40.707 | 21.3079 | 75.4528 | 45.1368 | 87.4555 | 213.1252
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 4.5602 | 5.3491 | 4.8934 | 6.1118 | 5.9652 | 5.4414 | 6.6176 | 6.7119 | 6.5975 | 7.023 | 7.2378 | 7.2097 | 7.6934 | 7.7757 | 8.4421 | 9.3493
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 4.5703 | 8.2032 | 5.1985 | 15.6979 | 5.9773 | 6.7781 | 6.8765 | 25.9364 | 13.3837 | 12.7996 | 47.9448 | 28.5176 | 83.1442 | 52.9105 | 95.8976 | 222.4745
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 576.5818 | 574.2756 | 580.9754 | 538.8875 | 464.9963 | 537.91 | 489.056 | 572.3266 | 519.5828 | 512.5035 | 589.3232 | 530.7967 | 648.9034 | 582.0954 | 666.4639 | 851.9286
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 175.4675 | 272.8653 | 249.9411 | 295.2868 | 154.0848 | 256.3246 | 278.0128 | 294.1615 | 269.4757 | 281.7316 | 295.4391 | 289.0423 | 326.6693 | 315.9277 | 324.0144 | 343.5248
| Feb | 182.3244 | 224.0699 | 186.6513 | 239.0685 | 147.0915 | 171.0543 | 167.6644 | 285.9487 | 241.3919 | 226.713 | 269.9848 | 231.8022 | 280.1549 | 274.1657 | 290.379 | 313.4324
| Mar | 184.1217 | 194.3429 | 191.3129 | 222.0063 | 150.3411 | 181.0278 | 194.6262 | 243.2797 | 209.101 | 241.6495 | 235.3667 | 231.6108 | 279.143 | 254.8729 | 280.1426 | 303.1386
| Apr | 191.9625 | 178.1349 | 193.3036 | 176.2701 | 158.7401 | 185.5867 | 180.7357 | 210.663 | 174.4664 | 209.8206 | 215.3911 | 171.3753 | 217.0683 | 180.0795 | 254.0304 | 260.1737
| May | 204.0291 | 213.7502 | 223.3072 | 182.5842 | 155.2547 | 212.2127 | 147.8993 | 172.4856 | 190.1702 | 160.6537 | 170.9134 | 176.1198 | 170.4473 | 153.5396 | 219.2219 | 181.1255
| Jun | 219.2951 | 215.9399 | 298.8869 | 197.3319 | 157.1618 | 289.2399 | 155.5493 | 215.6282 | 211.509 | 157.5294 | 204.8038 | 193.0981 | 202.233 | 187.7605 | 176.8031 | 152.852
| Jul | 212.729 | 223.4951 | 272.0561 | 221.6878 | 163.4472 | 260.256 | 167.48 | 221.7116 | 223.052 | 169.4557 | 210.0104 | 207.2096 | 201.4009 | 196.7261 | 193.5009 | 156.9243
| Aug | 221.2321 | 224.7185 | 279.7231 | 200.7326 | 189.0209 | 247.5186 | 161.7405 | 222.8675 | 208.4173 | 164.6691 | 207.8178 | 202.8374 | 199.3831 | 185.9037 | 183.8464 | 153.4683
| Sep | 210.7667 | 212.8004 | 238.2103 | 187.1152 | 175.4738 | 233.1461 | 197.2459 | 187.387 | 183.8282 | 166.4153 | 176.0892 | 183.3347 | 173.7885 | 168.9755 | 172.1546 | 204.9825
| Oct | 206.9715 | 191.4201 | 196.5815 | 169.1938 | 163.7149 | 189.8458 | 155.666 | 207.115 | 171.6585 | 209.7954 | 176.0011 | 187.1409 | 221.3665 | 209.7839 | 231.2508 | 286.0608
| Nov | 186.8355 | 177.0078 | 173.7548 | 184.8531 | 150.6234 | 161.8396 | 183.9754 | 244.9464 | 238.0959 | 225.122 | 239.5083 | 215.3112 | 271.6176 | 229.7724 | 286.8506 | 307.0661
| Dec | 173.6422 | 264.8675 | 269.9552 | 248.0778 | 155.6443 | 206.7492 | 248.3792 | 274.1328 | 251.2743 | 257.0484 | 279.4211 | 267.6781 | 278.095 | 293.513 | 286.6791 | 310.0761
Time of Peak Electrical Demand
| Jan | 23-JAN-16:10 | 17-JAN-06:10 | 02-JAN-06:10 | 02-JAN-08:09 | 26-JAN-13:00 | 02-JAN-06:10 | 02-JAN-06:10 | 02-JAN-08:09 | 02-JAN-08:09 | 02-JAN-08:09 | 02-JAN-08:09 | 02-JAN-08:09 | 02-JAN-08:09 | 02-JAN-08:09 | 02-JAN-08:09 | 02-JAN-08:09
| Feb | 22-FEB-16:10 | 13-FEB-06:10 | 23-FEB-06:10 | 14-FEB-06:10 | 13-FEB-11:00 | 06-FEB-06:10 | 06-FEB-08:09 | 21-FEB-06:10 | 06-FEB-06:10 | 13-FEB-06:10 | 06-FEB-06:10 | 21-FEB-06:10 | 06-FEB-06:10 | 27-FEB-08:09 | 06-FEB-06:10 | 06-FEB-08:09
| Mar | 13-MAR-15:30 | 20-MAR-05:10 | 17-MAR-15:50 | 13-MAR-05:10 | 30-MAR-12:39 | 06-MAR-06:10 | 16-MAR-07:10 | 13-MAR-05:10 | 13-MAR-05:10 | 20-MAR-05:10 | 20-MAR-05:10 | 06-MAR-06:10 | 06-MAR-06:10 | 06-MAR-06:10 | 06-MAR-06:10 | 13-MAR-07:10
| Apr | 04-APR-15:00 | 21-APR-15:30 | 26-APR-15:00 | 03-APR-05:10 | 11-APR-15:00 | 21-APR-15:30 | 24-APR-07:10 | 17-APR-05:10 | 21-APR-15:00 | 03-APR-05:10 | 03-APR-05:10 | 03-APR-07:10 | 24-APR-05:10 | 17-APR-05:10 | 03-APR-05:10 | 03-APR-07:10
| May | 24-MAY-14:00 | 18-MAY-15:30 | 30-MAY-15:00 | 31-MAY-15:00 | 30-MAY-07:00 | 31-MAY-15:00 | 01-MAY-07:10 | 31-MAY-15:00 | 31-MAY-15:00 | 18-MAY-07:10 | 30-MAY-15:00 | 23-MAY-15:00 | 31-MAY-12:09 | 12-MAY-07:10 | 01-MAY-05:10 | 01-MAY-05:10
| Jun | 27-JUN-15:20 | 13-JUN-15:30 | 08-JUN-15:00 | 19-JUN-15:50 | 28-JUN-12:00 | 27-JUN-15:50 | 16-JUN-15:00 | 30-JUN-15:00 | 20-JUN-15:00 | 28-JUN-15:30 | 08-JUN-12:00 | 27-JUN-15:00 | 29-JUN-15:00 | 26-JUN-15:00 | 14-JUN-15:00 | 20-JUN-15:00
| Jul | 13-JUL-15:20 | 05-JUL-15:00 | 11-JUL-15:00 | 03-JUL-15:00 | 20-JUL-15:09 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-15:00 | 24-JUL-15:09 | 13-JUL-15:09 | 17-JUL-15:30 | 13-JUL-15:00 | 21-JUL-15:00 | 06-JUL-15:00 | 21-JUL-15:00
| Aug | 21-AUG-15:09 | 31-AUG-15:00 | 01-AUG-15:00 | 14-AUG-15:00 | 08-AUG-15:09 | 04-AUG-15:00 | 03-AUG-07:10 | 17-AUG-15:00 | 01-AUG-15:20 | 18-AUG-15:39 | 04-AUG-15:50 | 29-AUG-15:00 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:30 | 28-AUG-07:10
| Sep | 11-SEP-15:09 | 15-SEP-15:09 | 11-SEP-15:30 | 11-SEP-12:00 | 25-SEP-15:30 | 01-SEP-14:00 | 28-SEP-15:09 | 08-SEP-15:20 | 20-SEP-15:00 | 01-SEP-15:00 | 06-SEP-12:30 | 06-SEP-15:09 | 14-SEP-15:09 | 01-SEP-15:00 | 07-SEP-15:09 | 25-SEP-05:10
| Oct | 06-OCT-15:20 | 06-OCT-15:00 | 02-OCT-15:09 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-15:09 | 31-OCT-12:00 | 30-OCT-05:10 | 13-OCT-15:09 | 30-OCT-05:10 | 21-OCT-05:10 | 10-OCT-05:10 | 16-OCT-05:10 | 16-OCT-05:10 | 16-OCT-05:10 | 30-OCT-07:10
| Nov | 01-NOV-12:09 | 06-NOV-06:10 | 13-NOV-13:00 | 15-NOV-06:10 | 09-NOV-16:00 | 27-NOV-06:10 | 27-NOV-06:10 | 20-NOV-06:10 | 20-NOV-06:10 | 27-NOV-06:10 | 20-NOV-06:10 | 24-NOV-06:10 | 27-NOV-06:10 | 27-NOV-06:10 | 27-NOV-06:10 | 06-NOV-08:09
| Dec | 15-DEC-13:00 | 11-DEC-06:10 | 26-DEC-06:10 | 18-DEC-06:10 | 19-DEC-13:09 | 26-DEC-06:10 | 26-DEC-06:10 | 26-DEC-06:10 | 26-DEC-06:10 | 11-DEC-06:10 | 26-DEC-08:09 | 11-DEC-08:09 | 18-DEC-06:10 | 18-DEC-08:09 | 11-DEC-06:10 | 26-DEC-08:09
Source Energy
| Total Source Energy (GJ) | 9477.88 | 10287.91 | 9101.76 | 8854.1 | 7110.52 | 9502.34 | 7472.57 | 9875.76 | 8440.74 | 4406.55 | 9825.3 | 8458.28 | 10140.28 | 9452.31 | 10291.99 | 12412.38
| Total Source Energy (MJ/m2) | 1902.35 | 2064.94 | 1826.86 | 1777.15 | 1427.19 | 1907.26 | 1499.86 | 1982.21 | 1694.18 | 884.46 | 1972.09 | 1697.7 | 2035.31 | 1897.22 | 2065.76 | 2491.35
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59
| Total Building | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59 | 174.59
Emissions
| Carbon Equivalent (kg) | 217515.01 | 262053.0416 | 241014.0149 | 224448.2442 | 74776.4623 | 248524.9808 | 78603.4439 | 206387.2066 | 287375.4201 | 51519.1285 | 403762.2285 | 286519.1261 | 275477.2246 | 272384.9738 | 278900.667 | 265111.7622
| CO2 (kg) | 503903.2472 | 657846.1522 | 567043.2523 | 510281.5912 | 199758.3606 | 588951.5171 | 209993.4692 | 464337.1175 | 670284.897 | 122973.4214 | 934095.6491 | 669049.8713 | 639444.3426 | 636209.8673 | 648005.623 | 671788.2589
| NOX (kg) | 887.6713 | 863.8131 | 957.3397 | 981.1841 | 171.029 | 964.5501 | 179.8001 | 921.0496 | 1173.0994 | 195.2646 | 1689.5278 | 1167.6063 | 1147.0797 | 1117.4224 | 1159.667 | 821.7028
| SO2 (kg) | 3388.5004 | 3736.8928 | 3204.268 | 2541.4812 | 1848.5189 | 4043.4053 | 1941.7988 | 2760.3642 | 3059.1768 | 534.5383 | 5049.3167 | 3035.5079 | 1848.0607 | 1955.5562 | 1863.7826 | 4434.6836
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0154 | 0.0105 | 0.0087 | 0.0093 | 0.0008 | 0.0076 | 0.0009 | 0.0111 | 0.0119 | 0.0021 | 0.0152 | 0.0118 | 0.0135 | 0.0136 | 0.0136 | 0.0151
| Water for Electricity (m3) | 419.3725 | 1274.71 | 23669.7 | 4520.76 | 11153.6 | 20165.5 | 11716.5 | 171.6794 | 3181.05 | 7065.54 | 1162.4 | 3156.42 | 1214.74 | 46390.6 | 1225.06 | 890.0134

## Picture
DOE Commercial Building Benchmark - Medium Office

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | 5.35 | 28.26 | 1473.56
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 1.51
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_OCC_SCH | Fraction | Through 12/31 | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 16.1 | 54.5 | 2841.79
|  |  | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.7 | 0.4 | 0.4 | 0.1 | 0.1 | 0.05 | 0.05 | 10.2
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 11.3 | 60.8 | 3170.29
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 4.3
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 15 | 83.75 | 4366.96
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8.75
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 12 | 99 | 5162.14
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 15
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 597.6 | 3596.4 | 187526.57
|  |  | Sat | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 608.4
|  |  | WinterDesign | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 640.8
|  |  | Other | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 640.8
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8 | 2743.2 | 143038.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 439.2
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 15 | 86 | 4484.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 11
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 307.2 | 2150.4 | 112128
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | 5.37 | 30.55 | 1592.96
|  |  | Sat, WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | 2.57
|  |  | Sun, Hol, Other | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 1.13
Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600