## BuildingSummary
Building Summary Retail new construction
|  | Value | Data Source
Program
| Building Name | Retail Reference Building new construction 90.1-2004
| Available Fuel Types | gas, electricity
| Principal Building Activity | Retail
Form
| Total Floor Area (m2) | 2294 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.3
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.254
| East | 0
| North | 0
| West | 0
| Total | 0.071
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | Back, CoreRetail, FrontRetail, PointofSale, FrontEntry
| Floor to Ceiling Height (m) | 6.1
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1177
| Net Dimensions - Total Area (m2) | 1093.1
| Wall to Skin Ratio | 0.34
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 2294
| Net Dimensions - Total Area (m2) | 2294
| Roof to Skin Ratio | 0.66
Window Dimensions (m2)
| South | 83.9
| East | 0
| North | 0
| West | 0
| Total Area (m2) | 83.9
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab-on-grade
| Dimensions - Total Area (m2) | 2294
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Internal Mass | 244.23
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 7764.95
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.27 | See Reference Buildings Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | N/A
| Fuel | N/A
| Thermal Efficiency (%) | N/A
| Temperature Setpoint (ºC ) | N/A
| Water Consumption (L ) | N/A

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Back_Space | Yes | 1 | 379.89 | 2317.33 | 6.1 | 416.1704 | 0 | 27.8709 | 13.6303 | 8.6111 | 8.0729 |  |  |  | 0.75 | 284.9175 |  | 0.37388
Core_Retail | Yes | 1 | 1600.48 | 9762.95 | 6.1 | 356.8603 | 0 | 6.1939 | 258.3982 | 18.2986 | 3.2292 |  |  |  | 1.5 | 2400.72 |  | 0.2182
Point_of_Sale | Yes | 1 | 150.81 | 919.94 | 6.1 | 189.8002 | 38.05 | 6.1939 | 24.3483 | 18.2986 | 21.5278 |  |  |  | 1.5 | 226.215 |  | 0.40297
Front_Retail | Yes | 1 | 150.81 | 919.94 | 6.1 | 189.8002 | 38.05 | 6.1939 | 24.3483 | 18.2986 | 3.2292 |  |  |  | 1.5 | 226.215 |  | 0.40297
Front_Entry | Yes | 1 | 12 | 73.2 | 6.1 | 24.38 | 7.83 | 6.1939 | 1.9374 | 11.8403 | 0 | [6 empty] | 1
Total Conditioned Zones |  |  | 2293.99 | 13993.36 |  | 1177.0111 | 83.9301 |  | 322.6626
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-2004 Tables 9.5.1 & 9.6.1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Commercial Reference Buildings Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
| Weighting Factor | 118.8919 | 1176.8857 | 268.525 | 1264.6022 |  | 662.793 | 101.3348 | 1349.3302 | 63.1496 | 227.0515 | 1817.9529 | 420.0056 | 502.6576 | 48.3359 | 57.5322 | 7.2126
Fabric | [6 empty] | weighting factor is for all of 3B
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.4207 | 0.4207 | 0.4207 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.1669 | 1.4327 | 1.4327 | 1.692 | 1.692 | 1.9569 | 2.2026
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.7933 | 2.849 | 2.849 | 2.849 | 2.849 | 2.7933 | 3.7175
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 3.241 | 3.241 | 3.241 | 5.835 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 3.241 | 2.615
| SHGC | 0.251 | 0.251 | 0.251 | 0.252 | 0.252 | 0.252 | 0.39 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.296
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.162 | 0.162 | 0.162 | 0.223 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.212
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
| R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | 35.161 | 32.2601 | 29.6139 | 25.9817 | 15.6742 | 19.0944 | 11.3638 | 28.5422 | 20.7761 | 16.6339 | 35.6645 | 26.8596 | 39.3343 | 28.9831 | 41.3448 | 33.9177
| PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | 154.4331 | 144.8116 | 130.9176 | 134.4669 | 105.3413 | 105.7925 | 52.1135 | 122.7962 | 85.3936 | 69.3676 | 117.3028 | 81.0041 | 114.9831 | 67.0551 | 86.8309 | 70.0877
| PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | 23.5171 | 24.5185 | 23.9995 | 20.7496 | 15.6973 | 14.9708 | 16.714 | 19.3032 | 14.2186 | 15.308 | 18.5857 | 13.7571 | 18.2382 | 13.6084 | 17.3116 | 15.8707
| PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | 19.9267 | 21.0927 | 21.3787 | 16.6099 | 12.2704 | 14.3398 | 13.4862 | 16.7351 | 10.956 | 12.1423 | 16.4784 | 12.8055 | 18.5439 | 13.6194 | 18.6257 | 15.8707
Heating (kW)
| FRONT_ENTRY UNIT HEATER COIL | 0.9537 | 2.0187 | 1.5556 | 1.7409 | 0.82641 | 1.3917 | 1.2051 | 2.0384 | 1.7518 | 1.5798 | 2.6254 | 2.2677 | 2.9421 | 2.851 | 3.0766 | 3.8652
| PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 17.0303 | 35.7749 | 28.904 | 31.7718 | 16.5304 | 26.5709 | 20.7487 | 37.2609 | 31.9595 | 29.3415 | 46.3212 | 40.0202 | 51.069 | 49.3535 | 52.7522 | 67.9079
| PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 92.9463 | 122.7018 | 103.523 | 132.3637 | 96.6681 | 111.911 | 106.8502 | 147.3445 | 117.0733 | 127.425 | 175.3158 | 144.2287 | 199.2191 | 188.1107 | 209.3373 | 277.2634
| PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 8.7581 | 18.5731 | 14.2737 | 17.2199 | 9.1088 | 13.7223 | 11.3225 | 20.3108 | 16.9432 | 15.7078 | 26.054 | 22.0188 | 29.1432 | 27.8546 | 30.3775 | 38.7948
| PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 8.7581 | 18.5731 | 14.2662 | 17.2201 | 9.1088 | 13.7216 | 11.3241 | 20.3118 | 16.9432 | 15.7079 | 26.0547 | 22.0175 | 29.1442 | 27.8564 | 30.3781 | 38.7948
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.67 | 3.67 | 3.5 | 3.5 | 3.67 | 3.5 | 3.5 | 3.5 | 3.5 | 3.3 | 3.5
| PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.3 | 3.23 | 3.23 | 3.3 | 3.23 | 3.23 | 3.23 | 3.3 | 3.23 | 3.3
| PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.67 | 3.67 | 3.5 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
| PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67 | 3.67
Heating Efficiency (%)
| FRONT_ENTRY UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78
| PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
HVAC Control - Economizer
| PSZ-AC:1_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer
| PSZ-AC:2_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC:3_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-AC:4_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| FRONT_ENTRY UNIT HEATERFAN | 0.04 | 0.09 | 0.07 | 0.08 | 0.04 | 0.06 | 0.05 | 0.09 | 0.09 | 0.07 | 0.11 | 0.12 | 0.13 | 0.14 | 0.14 | 0.17
| PSZ-AC:1_UNITARY_PACKAGE_FAN | 1.43 | 1.44 | 1.51 | 1.05 | 0.75 | 0.91 | 0.64 | 1.15 | 1.24 | 0.91 | 1.44 | 1.53 | 1.58 | 1.75 | 1.66 | 2.05
| PSZ-AC:2_UNITARY_PACKAGE_FAN | 6.22 | 5.83 | 5.27 | 5.41 | 4.58 | 4.26 | 2.84 | 4.95 | 4.6 | 3.53 | 4.72 | 4.29 | 4.63 | 3.97 | 3.5 | 4.23
| PSZ-AC:3_UNITARY_PACKAGE_FAN | 1.01 | 1.04 | 1.15 | 0.95 | 0.81 | 0.83 | 1.01 | 0.9 | 0.85 | 0.87 | 0.88 | 0.82 | 0.86 | 0.82 | 0.82 | 0.96
| PSZ-AC:4_UNITARY_PACKAGE_FAN | 0.8 | 0.85 | 0.96 | 0.67 | 0.56 | 0.64 | 0.8 | 0.67 | 0.6 | 0.66 | 0.66 | 0.69 | 0.75 | 0.82 | 0.8 | 0.96
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.084409 | 0.11982 | 0.1034 | 0.1025 | 0.1291 | 0.098519 | 0.14795 | 0.074702 | 0.037533 | 0.074474 | 0.052219 | 0.037555 | 0.059918 | 0.074178 | 0.058864 | 0.095056
| Total Cost ($/m2) | 15.97 | 20.61 | 17.99 | 15.32 | 16.99 | 14.68 | 17.1 | 10.7 | 5.21 | 9.29 | 7.24 | 5.03 | 8.25 | 9.74 | 7.14 | 12.63
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011451 | 0.008041 | 0.0080813 | 0.00947 | 0.008689 | 0.0076087 | 0.0085784 | 0.009644 | 0.0068632 | 0.0084232 | 0.0083002 | 0.0069018 | 0.0078613 | 0.0080898 | 0.0078564 | 0.0041301
| Total Cost ($/m2) | 0.02 | 0.73 | 0.59 | 1.63 | 0.42 | 0.94 | 1.56 | 3.09 | 1.56 | 2.74 | 3.73 | 2.31 | 4.63 | 4.12 | 6.11 | 5.07
Total Utility Costs
| Cost Intensity ($/m2) | 15.99 | 21.34 | 18.58 | 16.95 | 17.4 | 15.62 | 18.66 | 13.79 | 6.77 | 12.03 | 10.97 | 7.34 | 12.88 | 13.87 | 13.25 | 17.7
Energy - End Uses
Electricity (kWh)
| Heating | 13.8889 | 525 | 275 | 800 | 208.3333 | 416.6667 | 725 | 1377.7778 | 836.1111 | 1597.2222 | 2041.6667 | 1402.7778 | 2605.5556 | 2319.4444 | 3183.3333 | 5777.7778
| Cooling | 122847.2222 | 86319.4444 | 95036.1111 | 41936.1111 | 13191.6667 | 54477.7778 | 2961.1111 | 31300 | 25263.8889 | 4050 | 21200 | 14827.7778 | 17697.2222 | 8227.7778 | 4594.4444 | 1075
| Interior Lighting | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667 | 138966.6667
| Exterior Lighting | 36130.5556 | 36116.6667 | 36111.1111 | 36105.5556 | 36077.7778 | 36069.4444 | 36088.8889 | 36066.6667 | 36080.5556 | 36008.3333 | 36072.2222 | 36050 | 36047.2222 | 36038.8889 | 36019.4444 | 35800
| Interior Equipment | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 80744.4444 | 77408.3333 | 73561.1111 | 69805.5556 | 58133.3333 | 56583.3333 | 31172.2222 | 65536.1111 | 61855.5556 | 50305.5556 | 64688.8889 | 60688.8889 | 65277.7778 | 60494.4444 | 40319.4444 | 67852.7778
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 433927.7778 | 394563.8889 | 399175 | 342838.8889 | 301802.7778 | 341738.8889 | 265136.1111 | 328472.2222 | 318227.7778 | 286155.5556 | 318197.2222 | 307163.8889 | 315822.2222 | 301272.2222 | 278308.3333 | 304700
Gas (MJ)
| Heating | 4610 | 208420 | 167030 | 394640 | 110050 | 284580 | 416460 | 735030 | 522430 | 744880 | 1030350 | 769120 | 1352310 | 1169360 | 1784040 | 2815660
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 4610 | 208420 | 167030 | 394640 | 110050 | 284580 | 416460 | 735030 | 522430 | 744880 | 1030350 | 769120 | 1352310 | 1169360 | 1784040 | 2815660
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 1566750 | 1628850 | 1604060 | 1628870 | 1196530 | 1514840 | 1370950 | 1917530 | 1668050 | 1775040 | 2175850 | 1874910 | 2489270 | 2253940 | 2785950 | 3912580
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0.021796 | 0.82389 | 0.43156 | 1.2555 | 0.32694 | 0.65388 | 1.1378 | 2.1622 | 1.3121 | 2.5065 | 3.204 | 2.2014 | 4.0889 | 3.6399 | 4.9957 | 9.0672
| Cooling (elec) | 192.7864 | 135.4627 | 149.1419 | 65.8111 | 20.7019 | 85.493 | 4.6469 | 49.1197 | 39.6471 | 6.3557 | 33.2695 | 23.2695 | 27.7726 | 12.912 | 7.2101 | 1.687
| Interior Lighting (elec) | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829 | 218.0829
| Exterior Lighting (elec) | 56.7003 | 56.6785 | 56.6698 | 56.6611 | 56.6175 | 56.6044 | 56.6349 | 56.6001 | 56.6219 | 56.5085 | 56.6088 | 56.5739 | 56.5696 | 56.5565 | 56.526 | 56.1816
| Interior Equipment (elec) | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 126.7137 | 121.4783 | 115.4408 | 109.5471 | 91.2297 | 88.7972 | 48.9191 | 102.847 | 97.071 | 78.9454 | 101.5174 | 95.2402 | 102.4416 | 94.935 | 63.274 | 106.4826
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 680.9707 | 619.1962 | 626.4325 | 538.0233 | 473.6246 | 536.297 | 416.0829 | 515.4774 | 499.4006 | 449.0691 | 499.3527 | 482.0378 | 495.6255 | 472.7919 | 436.7543 | 478.1712
Gas (MJ/m2)
| Heating (gas) | 2.0096 | 90.8548 | 72.812 | 172.0321 | 47.9732 | 124.0546 | 181.5439 | 320.4155 | 227.7386 | 324.7093 | 449.1519 | 335.2761 | 589.5013 | 509.7494 | 777.7017 | 1227.4073
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 2.0096 | 90.8548 | 72.812 | 172.0321 | 47.9732 | 124.0546 | 181.5439 | 320.4155 | 227.7386 | 324.7093 | 449.1519 | 335.2761 | 589.5013 | 509.7494 | 777.7017 | 1227.4073
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 682.9803 | 710.051 | 699.2445 | 710.0598 | 521.5934 | 660.3516 | 597.6268 | 835.8929 | 727.1392 | 773.7784 | 948.5002 | 817.3139 | 1085.1268 | 982.5413 | 1214.456 | 1705.5785
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 93.0864 | 80.8303 | 75.8149 | 67.7458 | 69.8239 | 64.6818 | 59.8265 | 67.0591 | 65.8311 | 63.7751 | 67.2009 | 65.9861 | 67.6115 | 66.416 | 62.7627 | 69.2734
| Feb | 95.4442 | 81.0196 | 74.6346 | 63.487 | 65.5355 | 64.937 | 60.432 | 66.6144 | 65.7087 | 63.7228 | 66.7551 | 66.1881 | 67.1956 | 66.1006 | 62.7361 | 69.0693
| Mar | 97.55 | 85.2649 | 89.7713 | 68.1036 | 65.0951 | 64.7616 | 59.3233 | 66.3329 | 65.5762 | 63.552 | 66.4956 | 65.6455 | 66.8065 | 57.9872 | 62.1537 | 66.9078
| Apr | 103.6464 | 101.9917 | 95.16 | 81.7306 | 72.1569 | 82.8989 | 57.69 | 66.9789 | 72.9615 | 57.1446 | 60.6883 | 66.8514 | 60.1501 | 57.5386 | 54.0692 | 59.2322
| May | 112.709 | 112.0137 | 117.3766 | 91.5059 | 67.5262 | 95.2419 | 58.8039 | 79.8008 | 80.371 | 63.1281 | 78.9619 | 73.759 | 95.7356 | 65.9375 | 59.5201 | 58.5825
| Jun | 119.6015 | 114.7163 | 136.7721 | 101.6828 | 70.7939 | 111.493 | 60.5791 | 105.6155 | 91.867 | 67.633 | 99.1167 | 83.7477 | 97.7406 | 85.6081 | 71.8629 | 67.3927
| Jul | 116.0067 | 120.2214 | 134.3067 | 112.4133 | 77.3259 | 110.2355 | 67.2318 | 110.5923 | 95.7084 | 75.5458 | 103.1647 | 90.7485 | 102.719 | 86.2738 | 83.7923 | 71.6675
| Aug | 117.7187 | 119.5743 | 136.0643 | 105.1213 | 83.0132 | 108.1172 | 62.7274 | 111.6628 | 92.4982 | 72.3689 | 101.4542 | 90.8075 | 96.2737 | 81.4061 | 82.1532 | 67.2011
| Sep | 111.9206 | 117.3682 | 122.7211 | 94.6454 | 81.6289 | 104.4241 | 76.0035 | 91.9458 | 81.5597 | 85.6006 | 83.7352 | 82.5623 | 79.9888 | 74.2514 | 64.7078 | 58.5861
| Oct | 108.749 | 101.3903 | 96.3824 | 84.6971 | 74.7664 | 83.651 | 58.5314 | 76.9892 | 70.154 | 63.3671 | 72.4946 | 71.7199 | 69.4643 | 62.0109 | 61.6985 | 67.6798
| Nov | 100.5854 | 89.5704 | 87.199 | 68.1572 | 69.0888 | 67.9379 | 59.6654 | 71.7929 | 65.979 | 63.6826 | 70.2459 | 65.7433 | 66.8799 | 65.5774 | 62.398 | 68.273
| Dec | 95.3426 | 86.0066 | 73.6281 | 67.3507 | 68.0449 | 64.9901 | 59.74 | 66.7413 | 65.9425 | 63.8351 | 66.7876 | 66.2426 | 67.3936 | 66.4656 | 62.6662 | 68.9356
Time of Peak Electrical Demand
| Jan | 23-JAN-17:00 | 20-JAN-17:49 | 28-JAN-17:00 | 13-JAN-17:00 | 25-JAN-17:19 | 10-JAN-17:00 | 04-JAN-17:00 | 30-JAN-17:00 | 12-JAN-17:00 | 31-JAN-17:00 | 26-JAN-17:00 | 05-JAN-17:00 | 04-JAN-17:00 | 06-JAN-17:00 | 11-JAN-17:00 | 13-JAN-09:09
| Feb | 25-FEB-13:00 | 23-FEB-15:00 | 28-FEB-16:00 | 18-FEB-16:10 | 11-FEB-17:30 | 08-FEB-17:10 | 15-FEB-17:49 | 23-FEB-17:00 | 14-FEB-17:49 | 11-FEB-17:00 | 03-FEB-17:00 | 15-FEB-17:00 | 01-FEB-17:00 | 23-FEB-17:00 | 01-FEB-17:00 | 03-FEB-09:09
| Mar | 13-MAR-14:00 | 25-MAR-16:00 | 17-MAR-15:00 | 28-MAR-15:00 | 31-MAR-14:30 | 31-MAR-15:00 | 01-MAR-17:00 | 04-MAR-17:00 | 02-MAR-17:00 | 06-MAR-17:00 | 03-MAR-17:00 | 01-MAR-17:00 | 01-MAR-17:00 | 03-MAR-09:09 | 09-MAR-17:00 | 02-MAR-17:00
| Apr | 01-APR-15:00 | 29-APR-14:00 | 01-APR-16:00 | 15-APR-15:00 | 11-APR-15:00 | 21-APR-15:00 | 29-APR-13:00 | 05-APR-16:00 | 22-APR-13:00 | 29-APR-15:30 | 07-APR-14:00 | 25-APR-14:00 | 15-APR-12:00 | 04-APR-08:09 | 03-APR-08:09 | 10-APR-08:09
| May | 24-MAY-14:00 | 26-MAY-14:00 | 27-MAY-16:00 | 15-MAY-14:00 | 30-MAY-14:09 | 31-MAY-15:00 | 17-MAY-14:09 | 31-MAY-15:00 | 31-MAY-15:00 | 05-MAY-15:00 | 30-MAY-15:00 | 23-MAY-15:00 | 27-MAY-14:00 | 16-MAY-16:00 | 31-MAY-15:00 | 24-MAY-14:00
| Jun | 28-JUN-14:00 | 13-JUN-14:00 | 28-JUN-16:00 | 19-JUN-14:00 | 30-JUN-14:00 | 27-JUN-15:00 | 16-JUN-14:00 | 30-JUN-15:00 | 29-JUN-14:30 | 28-JUN-14:00 | 08-JUN-12:00 | 27-JUN-15:00 | 29-JUN-14:00 | 30-JUN-15:00 | 14-JUN-14:00 | 20-JUN-16:00
| Jul | 13-JUL-14:00 | 05-JUL-15:00 | 11-JUL-15:00 | 03-JUL-15:00 | 10-JUL-14:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:00 | 15-JUL-14:00 | 21-JUL-16:00 | 08-JUL-15:00 | 29-JUL-16:00
| Aug | 21-AUG-14:00 | 31-AUG-15:00 | 01-AUG-16:00 | 17-AUG-14:00 | 08-AUG-14:00 | 04-AUG-15:00 | 15-AUG-11:00 | 09-AUG-14:00 | 01-AUG-14:00 | 07-AUG-14:00 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-16:00 | 12-AUG-14:00 | 15-AUG-16:00
| Sep | 11-SEP-14:00 | 16-SEP-14:00 | 09-SEP-15:00 | 11-SEP-13:00 | 25-SEP-14:00 | 01-SEP-14:00 | 28-SEP-14:00 | 09-SEP-14:00 | 02-SEP-15:39 | 02-SEP-15:00 | 05-SEP-14:00 | 02-SEP-14:00 | 14-SEP-14:00 | 02-SEP-15:00 | 07-SEP-14:00 | 29-SEP-08:09
| Oct | 07-OCT-15:00 | 06-OCT-15:00 | 02-OCT-16:00 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-14:00 | 13-OCT-14:00 | 20-OCT-15:00 | 13-OCT-14:00 | 30-OCT-16:00 | 31-OCT-16:49 | 05-OCT-14:00 | 07-OCT-14:00 | 06-OCT-15:00 | 31-OCT-16:00 | 27-OCT-08:09
| Nov | 07-NOV-17:40 | 27-NOV-17:00 | 13-NOV-17:30 | 22-NOV-17:30 | 08-NOV-16:00 | 10-NOV-16:40 | 14-NOV-16:00 | 04-NOV-16:00 | 08-NOV-17:10 | 16-NOV-17:00 | 02-NOV-16:49 | 17-NOV-17:00 | 27-NOV-17:00 | 29-NOV-17:00 | 24-NOV-17:00 | 02-NOV-08:09
| Dec | 15-DEC-17:30 | 02-DEC-17:19 | 09-DEC-17:19 | 21-DEC-17:00 | 19-DEC-12:00 | 05-DEC-16:30 | 02-DEC-17:00 | 14-DEC-17:00 | 28-DEC-17:00 | 13-DEC-17:00 | 14-DEC-17:00 | 11-DEC-17:00 | 30-DEC-17:00 | 11-DEC-17:00 | 30-DEC-17:00 | 29-DEC-09:09
Source Energy
| Total Source Energy (GJ) | 5186.65 | 5386.6 | 4727.73 | 4582.87 | 3482.84 | 4711.42 | 3408.93 | 5031.28 | 4371.67 | 2607.95 | 5187.11 | 4508.89 | 5384.46 | 5046.94 | 5391.74 | 6992.89
| Total Source Energy (MJ/m2) | 2260.97 | 2348.13 | 2060.92 | 1997.77 | 1518.25 | 2053.81 | 1486.02 | 2193.24 | 1905.7 | 1136.86 | 2261.17 | 1965.52 | 2347.2 | 2200.07 | 2350.37 | 3048.35
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emissions
| Carbon Equivalent (kg) | 119087.7019 | 135369.4359 | 123513.3566 | 112723.5214 | 37254.7099 | 120392.1325 | 38495.3624 | 101894.7905 | 139416.4364 | 34274.1449 | 188226.0011 | 139345.1494 | 132489.6651 | 131182.8834 | 127434.276 | 136512.5365
| CO2 (kg) | 275801.6905 | 341108.5566 | 292085.0714 | 260246.6465 | 99899.0993 | 287822.2275 | 104423.5262 | 237073.7416 | 330120.9662 | 88317.8662 | 445100.5623 | 332441.9816 | 319677.2926 | 316992.9346 | 312567.6021 | 361472.4254
| NOX (kg) | 486.1997 | 443.9415 | 486.8635 | 481.4995 | 85.7898 | 461.1538 | 90.4934 | 432.206 | 556.1649 | 114.782 | 761.4693 | 549.3554 | 518.7487 | 509.8583 | 485.15 | 402.2546
| SO2 (kg) | 1857.3849 | 1882.1245 | 1605.2107 | 1203.471 | 878.2361 | 1879.9204 | 771.6273 | 1199.2542 | 1389.7795 | 221.3755 | 2144.6633 | 1341.53 | 745.7538 | 804.7468 | 657.332 | 1551.7951
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0085 | 0.0053 | 0.0044 | 0.0044 | 0.0004 | 0.0036 | 0.0004 | 0.0049 | 0.0055 | 0.0009 | 0.0066 | 0.0053 | 0.0056 | 0.0057 | 0.005 | 0.0056
| Water Environmental Factors (m3) | 229.8766 | 642.0013 | 11857.3 | 2140.55 | 5298.96 | 9375.3 | 4655.2 | 74.5757 | 1445.01 | 2923.6 | 493.6622 | 1394.77 | 489.9795 | 19083.8 | 431.7799 | 311.305

## Picture
DOE Commercial Building Benchmark - Retail
Back_Space
Core_Retail
Front_Entry
Point_of_Sale
Front_Retail

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | 13.7 | 80.65 | 4205.32
|  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | 12.15
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 8.75
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | 11.15 | 65.6 | 3420.57
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | 9.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 5.25
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | 7.2 | 43.5 | 2268.21
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 7.5
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 2.8
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 16.5 | 98.5 | 5136.07
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19.5
INFIL_FRONT_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 17.25 | 104.25 | 5435.89
|  |  | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 18
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 12.75
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 630 | 4428 | 230888.57
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 654
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
FRONT_ENTRY_COOLING | Temperature | Through 12/31 | All | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2160 | 15120 | 788400
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 455.4 | 3171.6 | 165376.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 91 | 4745
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11