## BuildingSummary
Building Summary Retail post-1980 construction
|  | Value | Data Source
Program
| Building Name | Retail Reference Building post-1980 construction
| Available Fuel Types | gas, electricity
| Principal Building Activity | Retail
Form
| Total Floor Area (m2) | 2294 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.3
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.254
| East | 0
| North | 0
| West | 0
| Total | 0.071
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | Back, CoreRetail, FrontRetail, PointofSale, FrontEntry
| Floor to Ceiling Height (m) | 6.1
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1177
| Net Dimensions - Total Area (m2) | 1093.1
| Wall to Skin Ratio | 0.34
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 2294
| Net Dimensions - Total Area (m2) | 2294
| Roof to Skin Ratio | 0.66
Window Dimensions (m2)
| South | 83.9
| East | 0
| North | 0
| West | 0
| Total Area (m2) | 83.9
| Operable area (m2) | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab-on-grade
| Dimensions - Total Area (m2) | 2294
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Internal Mass | 244.23
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 7764.95
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 1.01 | See Reference Buildings Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | N/A
| Fuel | N/A
| Thermal Efficiency (%) | N/A
| Temperature Setpoint (ºC ) | N/A
| Water Consumption (L ) | N/A

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Back_Space | Yes | 1 | 379.89 | 2317.33 | 6.1 | 416.1704 | 0 | 27.8709 | 13.6303 | 12.558 | 8.0729 |  |  |  | 0.75 | 284.9175 |  | 1.4021
Core_Retail | Yes | 1 | 1600.48 | 9762.95 | 6.1 | 356.8603 | 0 | 6.1939 | 258.3982 | 36.2662 | 3.2292 |  |  |  | 1.5 | 2400.72 |  | 0.81826
Point_of_Sale | Yes | 1 | 150.81 | 919.94 | 6.1 | 189.8002 | 38.05 | 6.1939 | 24.3483 | 36.2662 | 21.5278 |  |  |  | 1.5 | 226.215 |  | 1.5111
Front_Retail | Yes | 1 | 150.81 | 919.94 | 6.1 | 189.8002 | 38.05 | 6.1939 | 24.3483 | 36.2662 | 3.2292 |  |  |  | 1.5 | 226.215 |  | 1.5111
Front_Entry | Yes | 1 | 12 | 73.2 | 6.1 | 24.38 | 7.83 | 6.1939 | 1.9374 | 36.2662 | 0 | [6 empty] | 1
Total Conditioned Zones |  |  | 2293.99 | 13993.36 |  | 1177.0111 | 83.9301 |  | 322.6626
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Commercial Reference Buildings Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.4207 | 0.51787 | 0.42955 | 0.60716 | 0.4207 | 0.60716 | 0.4207 | 1.4684 | 0.92678 | 1.7606 | 1.7606 | 1.2579 | 2.4814 | 2.2272 | 2.8902 | 3.7453
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
| SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
| R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | 45.4225 | 53.4059 | 39.3331 | 63.2747 | 30.1123 | 42.5643 | 31.8593 | 62.8444 | 47.549 | 36.2796 | 82.1086 | 65.1894 | 91.0342 | 67.0285 | 96.6539 | 84.382
| PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | 200.3707 | 195.8078 | 172.5889 | 197.3719 | 152.6785 | 122.2899 | 94.3954 | 157.703 | 121.1947 | 104.7442 | 168.4572 | 131.5561 | 189.5777 | 151.1242 | 217.8082 | 195.6483
| PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | 31.9907 | 32.1641 | 30.4047 | 29.7388 | 25.3304 | 25.6192 | 20.697 | 27.962 | 19.6065 | 21.0123 | 35.9571 | 25.2911 | 34.033 | 28.9951 | 37.3383 | 37.908
| PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | 27.9068 | 27.8149 | 28.1195 | 27.2891 | 22.7055 | 22.5599 | 17.7279 | 27.4701 | 20.4144 | 17.7735 | 36.5939 | 26.8338 | 40.5961 | 29.216 | 40.2994 | 37.908
Heating (kW)
| FRONT_ENTRY UNIT HEATER COIL | 0.97095 | 1.9116 | 1.5171 | 2.1451 | 1.2562 | 1.7668 | 1.4806 | 1.9613 | 1.9199 | 1.5579 | 2.5336 | 2.2988 | 2.6916 | 2.6457 | 2.8016 | 3.6865
| PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 30.2979 | 57.3302 | 45.4415 | 67.5578 | 38.1936 | 52.5013 | 47.1928 | 68.9032 | 59.7083 | 53.0765 | 88.4598 | 75.7345 | 97.6238 | 92.993 | 101.5183 | 136.7696
| PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 92.9463 | 156.4048 | 116.6766 | 190.3228 | 97.2163 | 144.1343 | 123.494 | 213.846 | 172.6232 | 164.0522 | 280.3081 | 228.7125 | 315.3934 | 296.5356 | 329.6727 | 449.0763
| PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 14.1927 | 27.9273 | 21.3874 | 32.5986 | 17.6357 | 25.448 | 21.6984 | 34.0294 | 29.1677 | 26.4014 | 44.3027 | 37.3411 | 48.9998 | 46.4263 | 51.1747 | 68.9888
| PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 14.1944 | 27.9273 | 21.3802 | 32.6012 | 17.6316 | 25.4523 | 21.6912 | 34.0294 | 29.1677 | 26.4021 | 44.3029 | 37.3391 | 48.9997 | 46.4267 | 51.1746 | 68.9888
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | 3.3 | 3.3 | 3.5 | 3.3 | 3.5 | 3.3 | 3.5 | 3.3 | 3.3 | 3.5 | 3.23 | 3.3 | 3.23 | 3.3 | 3.23 | 3.23
| PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
| PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
| PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.67 | 3.5 | 3.5 | 3.67 | 3.5 | 3.5 | 3.3 | 3.5 | 3.3 | 3.5
Heating Efficiency (%)
| FRONT_ENTRY UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.78 | 0.8 | 0.8 | 0.8 | 0.78 | 0.8 | 0.8 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78
| PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78
HVAC Control - Economizer
| Water-Side Heat Recovery | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| Air to Air Heat Recovery for Cooling | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| Air to Air Heat Recovery for Heating | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| High-Temperature Geothermal* | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer
Fan Max Flow Rate (m3/s )
| FRONT_ENTRY UNIT HEATERFAN | 0.04 | 0.08 | 0.07 | 0.1 | 0.05 | 0.08 | 0.06 | 0.08 | 0.1 | 0.07 | 0.11 | 0.12 | 0.12 | 0.13 | 0.13 | 0.16
| PSZ-AC:1_UNITARY_PACKAGE_FAN | 1.83 | 2.15 | 1.8 | 2.62 | 1.45 | 2.13 | 1.79 | 2.53 | 2.71 | 1.96 | 3.31 | 3.41 | 3.67 | 3.93 | 3.89 | 5.08
| PSZ-AC:2_UNITARY_PACKAGE_FAN | 8.07 | 7.89 | 7.69 | 7.95 | 7.38 | 6.47 | 5.3 | 6.64 | 6.78 | 5.51 | 7.21 | 7.11 | 8.19 | 8.77 | 8.77 | 11.82
| PSZ-AC:3_UNITARY_PACKAGE_FAN | 1.3 | 1.3 | 1.43 | 1.3 | 1.36 | 1.32 | 1.25 | 1.15 | 1.18 | 1.24 | 1.47 | 1.51 | 1.63 | 1.75 | 1.75 | 2.29
| PSZ-AC:4_UNITARY_PACKAGE_FAN | 1.12 | 1.12 | 1.25 | 1.13 | 1.18 | 1.12 | 1.07 | 1.11 | 1.18 | 1.02 | 1.47 | 1.51 | 1.63 | 1.75 | 1.75 | 2.29
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.085427 | 0.11887 | 0.097735 | 0.10028 | 0.12917 | 0.0983 | 0.14754 | 0.074964 | 0.037308 | 0.074621 | 0.093097 | 0.03731 | 0.059479 | 0.074343 | 0.05831 | 0.094236
| Total Cost ($/m2) | 23.78 | 30.67 | 25.39 | 23.84 | 27.57 | 23.32 | 29.02 | 16.69 | 8.24 | 14.86 | 20.82 | 8.19 | 13.98 | 17.33 | 13.52 | 23.52
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011432 | 0.0080449 | 0.0080907 | 0.0094622 | 0.0086807 | 0.007603 | 0.0085968 | 0.009649 | 0.0068556 | 0.0084204 | 0.0082903 | 0.0068915 | 0.0078757 | 0.0080449 | 0.0078594 | 0.0041197
| Total Cost ($/m2) | 0.06 | 1.05 | 0.76 | 2.67 | 0.68 | 1.33 | 2.18 | 4.69 | 2.35 | 3.65 | 5.58 | 3.38 | 6.72 | 5.49 | 8.25 | 7.29
Total Utility Costs
| Cost Intensity ($/m2) | 23.84 | 31.72 | 26.14 | 26.51 | 28.25 | 24.65 | 31.2 | 21.38 | 10.59 | 18.51 | 26.4 | 11.57 | 20.7 | 22.81 | 21.77 | 30.81
Energy - End Uses
Electricity (kWh)
| Heating | 13.8889 | 447.2222 | 238.8889 | 830.5556 | 208.3333 | 386.1111 | 675 | 1194.4444 | 783.3333 | 1358.3333 | 1727.7778 | 1238.8889 | 2077.7778 | 1872.2222 | 2511.1111 | 4666.6667
| Cooling | 166186.1111 | 117361.1111 | 124455.5556 | 66413.8889 | 24177.7778 | 83600 | 5069.4444 | 44902.7778 | 38427.7778 | 6522.2222 | 31747.2222 | 23497.2222 | 27041.6667 | 14111.1111 | 8552.7778 | 3433.3333
| Interior Lighting | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444
| Exterior Lighting | 43688.8889 | 43672.2222 | 43663.8889 | 43655.5556 | 43622.2222 | 43613.8889 | 43636.1111 | 43611.1111 | 43627.7778 | 43538.8889 | 43616.6667 | 43591.6667 | 43588.8889 | 43577.7778 | 43552.7778 | 43286.1111
| Interior Equipment | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 103811.1111 | 105513.8889 | 102511.1111 | 109561.1111 | 96705.5556 | 91611.1111 | 76916.6667 | 96005.5556 | 98808.3333 | 80286.1111 | 110877.7778 | 110350 | 141447.2222 | 150180.5556 | 152383.3333 | 196269.4444
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 638669.4444 | 591966.6667 | 595841.6667 | 545436.1111 | 489688.8889 | 544180.5556 | 451272.2222 | 510686.1111 | 506619.4444 | 456677.7778 | 512938.8889 | 503650 | 539122.2222 | 534713.8889 | 531969.4444 | 572627.7778
Gas (MJ)
| Heating | 11900 | 299380 | 215060 | 646670 | 179720 | 400250 | 581520 | 1115550 | 785150 | 994500 | 1544830 | 1124530 | 1958630 | 1564290 | 2407600 | 4058080
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 11900 | 299380 | 215060 | 646670 | 179720 | 400250 | 581520 | 1115550 | 785150 | 994500 | 1544830 | 1124530 | 1958630 | 1564290 | 2407600 | 4058080
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 2311110 | 2430460 | 2360090 | 2610240 | 1942600 | 2359300 | 2206090 | 2954020 | 2608980 | 2638530 | 3391410 | 2937670 | 3899480 | 3489260 | 4322690 | 6119540
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0.021796 | 0.70183 | 0.37489 | 1.3034 | 0.32694 | 0.60593 | 1.0593 | 1.8745 | 1.2293 | 2.1317 | 2.7114 | 1.9442 | 3.2607 | 2.9381 | 3.9407 | 7.3235
| Cooling (elec) | 260.7989 | 184.1769 | 195.3104 | 104.2245 | 37.9426 | 131.195 | 7.9556 | 70.4667 | 60.3054 | 10.2354 | 49.8215 | 36.8746 | 42.437 | 22.1448 | 13.422 | 5.388
| Interior Lighting (elec) | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148
| Exterior Lighting (elec) | 68.5618 | 68.5356 | 68.5225 | 68.5095 | 68.4571 | 68.4441 | 68.4789 | 68.4397 | 68.4659 | 68.3264 | 68.4484 | 68.4092 | 68.4048 | 68.3874 | 68.3482 | 67.9297
| Interior Equipment (elec) | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 162.9127 | 165.5849 | 160.8725 | 171.9362 | 151.7618 | 143.767 | 120.7067 | 150.6633 | 155.0617 | 125.9944 | 174.0025 | 173.1743 | 221.9757 | 235.6811 | 239.1379 | 308.0092
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1002.2755 | 928.984 | 935.0651 | 855.9628 | 768.4776 | 853.9924 | 708.1897 | 801.429 | 795.0471 | 716.6727 | 804.9643 | 790.3871 | 846.0543 | 839.1362 | 834.8293 | 898.6351
Gas (MJ/m2)
| Heating (gas) | 5.1875 | 130.5062 | 93.7493 | 281.8975 | 78.3438 | 174.4777 | 253.4972 | 486.2924 | 342.2639 | 433.5241 | 673.4249 | 490.207 | 853.8093 | 681.9079 | 1049.5251 | 1769.0051
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 5.1875 | 130.5062 | 93.7493 | 281.8975 | 78.3438 | 174.4777 | 253.4972 | 486.2924 | 342.2639 | 433.5241 | 673.4249 | 490.207 | 853.8093 | 681.9079 | 1049.5251 | 1769.0051
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 1007.463 | 1059.4902 | 1028.8144 | 1137.8602 | 846.8215 | 1028.47 | 961.6825 | 1287.7214 | 1137.311 | 1150.1925 | 1478.3892 | 1280.5941 | 1699.8679 | 1521.0441 | 1884.3543 | 2667.6402
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 140.1579 | 128.2013 | 119.5134 | 110.2845 | 118.9987 | 105.2627 | 102.4675 | 106.356 | 106.4768 | 103.1875 | 109.1875 | 108.8425 | 114.8112 | 116.3498 | 116.4352 | 125.3191
| Feb | 145.5468 | 128.5948 | 117.9471 | 108.6026 | 114.2785 | 106.4389 | 106.7068 | 105.9148 | 106.9859 | 103.1781 | 108.784 | 108.9938 | 114.435 | 116.0959 | 116.4631 | 125.1299
| Mar | 148.0318 | 134.1518 | 136.8148 | 116.1199 | 116.2299 | 109.791 | 102.0352 | 109.6957 | 106.8393 | 102.9824 | 108.5621 | 108.4842 | 114.0361 | 107.5056 | 115.9202 | 122.9008
| Apr | 155.7623 | 154.0632 | 143.0666 | 136.1736 | 125.8575 | 134.4288 | 106.6179 | 111.758 | 122.1022 | 98.509 | 104.6556 | 114.4908 | 113.9448 | 105.8977 | 106.1745 | 113.5413
| May | 169.4895 | 167.993 | 170.798 | 149.0707 | 121.0924 | 151.6357 | 108.5476 | 128.7736 | 131.613 | 107.777 | 132.0007 | 124.4923 | 162.2411 | 122.9817 | 119.1406 | 115.4472
| Jun | 177.7921 | 171.5563 | 197.5875 | 164.2464 | 123.2767 | 170.6616 | 111.7323 | 161.9125 | 146.9153 | 113.3082 | 158.4532 | 138.1521 | 161.0543 | 151.3743 | 138.1843 | 134.4025
| Jul | 172.4723 | 178.2648 | 193.697 | 180.3256 | 131.6893 | 168.1153 | 123.6548 | 168.9743 | 152.6435 | 124.7055 | 162.3993 | 147.1423 | 168.0478 | 152.0571 | 153.9318 | 141.4553
| Aug | 175.9343 | 176.7768 | 196.5962 | 168.0745 | 141.0231 | 165.307 | 115.0787 | 167.9707 | 148.1525 | 119.8949 | 159.2075 | 147.6659 | 158.6775 | 146.0437 | 151.5798 | 134.2303
| Sep | 167.1602 | 173.0914 | 177.4362 | 152.6308 | 139.5097 | 162.2212 | 135.2484 | 142.5585 | 132.2826 | 139.8209 | 136.706 | 136.7157 | 138.2826 | 135.299 | 127.9378 | 113.8432
| Oct | 162.4866 | 153.4817 | 144.6482 | 140.2356 | 128.1106 | 135.8516 | 107.5139 | 124.7058 | 117.373 | 102.8124 | 121.996 | 121.6535 | 124.1164 | 117.6797 | 123.2934 | 123.7804
| Nov | 150.0108 | 139.2981 | 133.668 | 113.8511 | 118.8633 | 112.2175 | 102.2916 | 117.2461 | 107.1323 | 103.1416 | 118.5061 | 108.5503 | 114.1326 | 115.6264 | 116.1439 | 124.3629
| Dec | 143.5683 | 135.2773 | 116.6901 | 108.7145 | 120.352 | 106.5974 | 102.4298 | 106.0032 | 106.5853 | 103.2956 | 108.786 | 109.0503 | 114.6397 | 116.4338 | 116.4021 | 124.9964
Time of Peak Electrical Demand
| Jan | 23-JAN-17:00 | 20-JAN-17:49 | 28-JAN-17:00 | 23-JAN-17:00 | 26-JAN-13:00 | 10-JAN-17:00 | 04-JAN-17:49 | 17-JAN-17:00 | 12-JAN-17:00 | 31-JAN-17:00 | 26-JAN-17:00 | 05-JAN-17:00 | 04-JAN-17:00 | 06-JAN-17:00 | 09-JAN-17:00 | 13-JAN-09:09
| Feb | 25-FEB-13:00 | 23-FEB-15:00 | 28-FEB-16:00 | 18-FEB-15:00 | 13-FEB-11:00 | 08-FEB-17:10 | 15-FEB-17:49 | 23-FEB-17:00 | 14-FEB-17:49 | 11-FEB-17:00 | 03-FEB-17:00 | 15-FEB-17:00 | 03-FEB-17:00 | 23-FEB-17:00 | 01-FEB-17:00 | 03-FEB-09:09
| Mar | 13-MAR-14:00 | 25-MAR-16:00 | 17-MAR-15:00 | 28-MAR-15:00 | 31-MAR-14:09 | 31-MAR-15:00 | 01-MAR-17:00 | 09-MAR-15:00 | 02-MAR-17:00 | 06-MAR-17:00 | 03-MAR-17:00 | 01-MAR-17:00 | 01-MAR-17:00 | 30-MAR-16:00 | 08-MAR-17:00 | 02-MAR-17:00
| Apr | 01-APR-15:00 | 29-APR-14:39 | 01-APR-16:00 | 15-APR-15:00 | 11-APR-15:00 | 21-APR-15:00 | 29-APR-14:39 | 04-APR-15:00 | 22-APR-13:00 | 29-APR-14:00 | 07-APR-14:00 | 25-APR-14:00 | 01-APR-16:00 | 04-APR-08:09 | 03-APR-08:09 | 10-APR-08:09
| May | 24-MAY-14:00 | 26-MAY-14:00 | 27-MAY-16:00 | 15-MAY-14:00 | 30-MAY-12:00 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-15:00 | 05-MAY-15:00 | 30-MAY-15:00 | 23-MAY-15:00 | 27-MAY-14:00 | 16-MAY-16:00 | 31-MAY-15:00 | 24-MAY-14:00
| Jun | 28-JUN-14:00 | 13-JUN-14:00 | 28-JUN-16:00 | 19-JUN-14:00 | 30-JUN-14:00 | 27-JUN-15:00 | 16-JUN-14:00 | 30-JUN-16:00 | 29-JUN-14:09 | 28-JUN-14:00 | 08-JUN-12:00 | 28-JUN-13:00 | 29-JUN-14:00 | 30-JUN-15:00 | 14-JUN-14:00 | 20-JUN-16:00
| Jul | 13-JUL-14:00 | 18-JUL-12:00 | 11-JUL-15:00 | 03-JUL-15:00 | 10-JUL-14:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:00 | 15-JUL-14:00 | 21-JUL-16:00 | 08-JUL-15:00 | 29-JUL-16:00
| Aug | 21-AUG-14:00 | 31-AUG-15:00 | 01-AUG-16:00 | 17-AUG-14:00 | 08-AUG-12:00 | 04-AUG-15:00 | 15-AUG-11:00 | 17-AUG-14:00 | 01-AUG-14:00 | 07-AUG-14:00 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-16:00 | 09-AUG-16:00 | 12-AUG-14:00 | 15-AUG-16:00
| Sep | 11-SEP-14:00 | 16-SEP-14:00 | 09-SEP-15:00 | 11-SEP-13:00 | 23-SEP-13:00 | 01-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 02-SEP-14:00 | 02-SEP-15:00 | 27-SEP-15:00 | 02-SEP-14:00 | 14-SEP-14:00 | 01-SEP-16:00 | 07-SEP-14:00 | 02-SEP-14:00
| Oct | 07-OCT-15:00 | 06-OCT-15:00 | 02-OCT-16:00 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-15:00 | 13-OCT-15:00 | 20-OCT-15:00 | 13-OCT-14:00 | 30-OCT-16:00 | 31-OCT-16:49 | 05-OCT-14:00 | 07-OCT-14:00 | 06-OCT-16:00 | 07-OCT-14:00 | 27-OCT-08:09
| Nov | 07-NOV-17:40 | 27-NOV-17:00 | 13-NOV-17:30 | 22-NOV-17:30 | 20-NOV-12:00 | 10-NOV-16:40 | 14-NOV-16:00 | 04-NOV-16:00 | 08-NOV-17:10 | 16-NOV-17:00 | 02-NOV-16:49 | 17-NOV-17:00 | 27-NOV-17:00 | 29-NOV-17:00 | 24-NOV-17:00 | 02-NOV-08:09
| Dec | 15-DEC-17:30 | 02-DEC-17:19 | 09-DEC-17:19 | 16-DEC-17:00 | 19-DEC-12:00 | 05-DEC-16:30 | 27-DEC-17:00 | 14-DEC-17:00 | 28-DEC-17:00 | 13-DEC-17:00 | 14-DEC-17:00 | 11-DEC-17:00 | 30-DEC-17:00 | 11-DEC-17:00 | 30-DEC-17:00 | 29-DEC-09:09
Source Energy
| Total Source Energy (GJ) | 7639.48 | 8067 | 7019.57 | 7311.61 | 5652.36 | 7444.61 | 5663.08 | 7792.55 | 6908.84 | 3949.9 | 8234.94 | 7243.99 | 8809.51 | 8399.4 | 9211.27 | 11794.94
| Total Source Energy (MJ/m2) | 3330.21 | 3516.58 | 3059.98 | 3187.28 | 2463.99 | 3245.26 | 2468.66 | 3396.94 | 3011.71 | 1721.85 | 3589.78 | 3157.81 | 3840.25 | 3661.47 | 4015.39 | 5141.66
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emissions
| Carbon Equivalent (kg) | 175369.5102 | 202855.4368 | 183748.0955 | 179675.3115 | 60468.6714 | 190756.5123 | 63224.53 | 157927.9245 | 221111.0527 | 51195.1321 | 301330.9102 | 226018.5515 | 219857.644 | 223612.8118 | 225505.0821 | 234308.0344
| CO2 (kg) | 406200.6705 | 511073.4192 | 434204.5362 | 415016.351 | 162152.0628 | 455567.1803 | 171099.1429 | 367167.2127 | 523126.1609 | 130825.7083 | 711463.0687 | 537982.6686 | 527477.8646 | 535984.7155 | 545223.9866 | 615058.9602
| NOX (kg) | 715.847 | 665.4182 | 725.1109 | 766.9251 | 139.2534 | 731.8317 | 148.0007 | 670.6757 | 883.2108 | 173.9922 | 1222.0144 | 894.3069 | 868.9812 | 880.7457 | 879.9159 | 697.6222
| SO2 (kg) | 2733.7627 | 2823.7585 | 2396.0567 | 1914.6505 | 1424.984 | 2993.5428 | 1313.3008 | 1864.5084 | 2212.5116 | 353.2411 | 3457.217 | 2199.6432 | 1272.9429 | 1428.1695 | 1256.1787 | 2915.9853
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0125 | 0.008 | 0.0065 | 0.0071 | 0.0007 | 0.0056 | 0.0007 | 0.0076 | 0.0087 | 0.0015 | 0.0106 | 0.0087 | 0.0095 | 0.0101 | 0.0094 | 0.0103
| Water Environmental Factors (m3) | 338.3401 | 963.1982 | 17699.1 | 3405.48 | 8597.84 | 14929.1 | 7923.31 | 115.945 | 2300.45 | 4665.78 | 795.7952 | 2286.98 | 836.418 | 33871 | 825.3191 | 585.041

## Picture
DOE Commercial Building Benchmark - Retail
Back_Space
Core_Retail
Front_Entry
Point_of_Sale
Front_Retail

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ALWAYS_ON | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | 13.7 | 80.65 | 4205.32
|  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | 12.15
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 8.75
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | 11.15 | 65.6 | 3420.57
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | 9.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 5.25
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | 7.2 | 43.5 | 2268.21
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 7.5
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 2.8
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 16.5 | 98.5 | 5136.07
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19.5
INFIL_FRONT_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 17.25 | 104.25 | 5435.89
|  |  | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 18
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 12.75
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 630 | 4428 | 230888.57
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 654
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
FRONT_ENTRY_COOLING | Temperature | Through 12/31 | All | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2160 | 15120 | 788400
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 455.4 | 3171.6 | 165376.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 91 | 4745
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11