## Sheet1
Component | Variable | Value | Units | Description | sample values | allowed
Delivery | gasdeliverycapable | 1 | logical [0,1] | Gas delivery to station |  | 0 | 1
Delivery | liquiddeliverycapable | 0 | logical [0,1] | Liquid delivery to station |  | 0 | 1
Production | productioncapable | 0 | logical [0,1] | On-site production at station |  | 0 | 1
Storage | hpstoragecapable | 1 | logical [0,1] | High pressure storage at station |  | 0 | 1
Storage | mpstoragecapable | 0 | logical [0,1] | Medium pressure storage at station |  | 0 | 1
Storage | lpstoragecapable | 1 | logical [0,1] | Low pressure storage at station |  | 0 | 1
Production | SOCForProduction | 0 | % | Storage level trigger for production | 90 | 0 | 150
Production | effElyzr | 0 | kWh/kg | Production unit efficiency | 54.3 | 0 | 150
Production | Felectrolyzer_kgperh | 0 | kg/h | flow/production rate | 0 | 0 | 100
Production | PmaxElectrolyzer | 0 | MPa | output max pressure | 0 | 0 | 120
Storage | VhpBank | 0.42 | m3 | Volume high pressure (HP) bank %HITRF: 0.342925 | 0.33 | 0 | 100
Storage | VmpBank | 0 | m3 | Volume medium pressure (MP) bank %HITRF: 1.3224; | 1 | 0 | 100
Storage | VlpBank | 3 | m3 | Volume low pressure (LP) bank %Default: 2.6108; | 2.6 | 0 | 100
Storage | VlqBank | 0 | m3 | Volume of liquid (LQ) bank (22.7125 = 6000 gallons) | 0 | 0 | 100
Storage | numHPbanks | 4 | # | Number of high prssure banks | 3 | 0 | 100
Storage | numMPbanks | 0 | # | Number of medium pressure banks | 1 | 0 | 100
Storage | numLPbanks | 9 | # | Number of low pressure banks | 3 | 0 | 100
Storage | numLQbanks | 0 | # | Number of liquid banks | 0 | 0 | 100
Storage | PhpBankMin | 45 | Mpa | Minimum HP bank pressure (Must use whole numbers or adjust pressure lookup function, Must adjust dispensing algorithm if min Php is less than or equal to 0) | 45 | 0 | 120
Storage | PmpBankMin | 0 | MPa | Minimum MP bank pressure (Must use whole numbers or adjust pressure lookup function, Must adjust dispensing algorithm if min Pmp is less than or equal to 0) | 0 | 0 | 120
Storage | PlpBankMin | 0 | MPa | Minimum LP bank pressure | 0 | 0 | 120
Storage | PhpBankMax | 90 | MPa | Maximum HP bank pressure | 90 | 0 | 120
Storage | PmpBankMax | 0 | MPa | Maximum MP bank pressure | 41 | 0 | 120
Storage | PlpBankMax | 50 | MPa | Maximum LP bank pressure | 24 | 0 | 120
Storage | PvapStart | 0 | MPa | Vaporizer output pressure (must be greater than MP compressor minimum) (www.linde-engineering.com.hk/internet.le.le.hkg/zt/images/P_3_4_e_10_150dpi227_5776.pdf?v=.) |  | 0 | 120
Storage | hpDispense | 1 | logical [0,1] | High pressure bank Eligible for fill, 1=eligible, 0=not eligible | 1 | 0 | 1
Storage | mpDispense | 0 | logical [0,1] | Medium pressure bank Eligible for fill, 1=eligible, 0=not eligible | 1 | 0 | 1
Storage | lpDispense | 1 | logical [0,1] | Low pressure bank Eligible for fill, 1=eligible, 0=not eligible | 1
Compressor | AllowDirectCompress | 1 | logical [0,1] | Allow compressor to fill bank which are used for dispensing?, 1=yes, 0=no. | 1 | 0 | 100
Compressor | NumHPc | 1 | # | Number of high pressure compressors | 1
Compressor | NumMPc | 0 | # | Number of medium pressure compressors | 1 | 0 | 100
Compressor | PminHPc | 5 | MPa | Minimum High pressure compressor (HPc) pressure | 20 | 0 | 120
Compressor | PminMPc | 0 | MPa | Minimum Medium pressure compressor (MPc) pressure | 0.5 | 0 | 120
Compressor | PmaxHPc | 90 | Mpa | Maximum HPc pressure | 93 | 0 | 120
Compressor | PmaxMPc | 0 | Mpa | Maximum MPc pressure | 42 | 0 | 120
Compressor | Fhp1 | 75 | kg/h | HPc maximum flowrate | 10 | 0 | 250
Compressor | Fmp1 | 0 | kg/h | MPc maximum flowrate | 5 | 0 | 100
Compressor | Flq1 | 0 | kg/h | Liquid pump maximum flowrate | 200 | 0 | 100
Compressor | Fvap1 | 0 | kg/h | Vaporizer maximum flowrate | 200 | 0 | 100
Compressor | effHP | 4 | kWh/kg | HPc efficinecy (includes BOP) | 4 | 0 | 100
Compressor | effMP | 2 | kWh/kg | MPc efficiency (includes BOP) | 2 | 0 | 100
Chiller | setPointPC | -35 | degC | Pre-cooling setpoint | -35 | -45 | 40
Chiller | effPC | 1.5 | kWh/kg | Pre-cooling efficiency | 1.5 | 0 | 100
Chiller | powerPC | 0 | kW | fixed Pre-cooling power | 0 | 0 | 100
Chiller | recTimePC | 1800 | s |  | 1800 | 0 | 7200
Dispenser | staTemp | 20 | degC | Ambient temperature | 25 | 0 | 40
Dispenser | max_disp | 1 | # | Maximum number fueling positions capable of simultaneous fill | 1 | 0 | 4
Delivery | startMassDel | 300 | kg | Mass per delivery | 0 | 0 | 1000
Delivery | numDeliveries | 1 | #/day | Number of deliveries per day | 0 | 0 | 2
Delivery | numBanksDel | 6 | # | Number of banks delivering hydrogen | 0 | 0 | 100
Delivery | Pdel | 35 | MPa | Pressure of delivery truck | 0 | 0 | 120
Delivery | Fdel | 1 | kg/s | Delivery flow rate | 1 | 0 | 5
Delivery | Del_wait_time | 3600 | s | Delivery truck dwell time | 3600 | 0 | 14400
Delivery | Delivery_type | 1 | selector [1,2] | Fuel delivery type, 1=gaseous, 2=liquid | 1 | 1 | 2
Liquid | FlqTruck | 0 | kg/s | Liquid truck delivery rate to storage | 0.4464 | 0 | 5
Liquid | effPmpLQ | 0 | kWh/kg | Liquid pump efficiency (kWh/kg of station capacity) (HRSAM v1.1) | 0.6644 | 0 | 5
Liquid | effRef | 0 | kWh/kg | Refrigeration efficiency (HRSAM v1.1) (is this more representative as a constant (kW/s) or as specific energy consumption (kW/kg/s) | 0.26 | 0 | 5
Liquid | BoilOff | 0 | kg/day | Boil-off (HRSAM v1.1 for 200kg/day capacity station) (Not wired up yet, consider calculating boil-off based on physical properties) | 0 | 0 | 100
Liquid | effVAP | 0 | kWh/kg | Vaporizer efficiency (HRSAM, Evaporator heated by natural draft so no effect) | 0 | 0 | 100